## TEFC Annual Estimated Savings
Estimated Annual Energy Savings with NEMA Premium® Motors1 TEFC · 1800 RPM · Full-load Operation · Nominal Efficiency3 Estimated Annual Energy Cost = (Hp x annual operating hours x cost of electricity x 0.746) / (efficiency)
Learn more about saving money through sound motor management. For additional tools and resources, visit www.motorsmatter.org.
|  | Enter Appropriate Values for: |  | Annual Operating Hours : |  |  | 8000 | hrs per year
|  |  |  | Cost of Electricity : |  |  | 10 | ¢ per kWh
Motor Size2 (hp) | Estimated Annual Operating Costs |  | Estimated Annual Energy Savings | Estimated Annual Operating Costs |  | Estimated Annual Energy Savings |  | Estimated Annual Operating Costs |  | Estimated Annual Energy Savings
| Pre-EPAct Motors | EPAct Motors | Pre-EPAct → EPAct | EPAct Motors | NEMA Prem Motors | EPAct → NEMA Prem |  | Pre-EPAct Motors | NEMA Prem Motors | Pre-EPAct → NEMA Prem
1 | 778.0965 | 723.3939 | 54.7025 | 723.3939 | 698.0117 | 25.3822 |  | 778.0965 | 698.0117 | 80.0848
1.5 | 1131.732 | 1065.7143 | 66.0177 | 1065.7143 | 1034.9133 | 30.801 |  | 1131.732 | 1034.9133 | 96.8187
2 | 1477.2277 | 1420.9524 | 56.2753 | 1420.9524 | 1379.8844 | 41.068 |  | 1477.2277 | 1379.8844 | 97.3433
3 | 2199.5086 | 2046.1714 | 153.3372 | 2046.1714 | 2000.4469 | 45.7245 |  | 2199.5086 | 2000.4469 | 199.0617
5 | 3582.2329 | 3410.2857 | 171.9472 | 3410.2857 | 3334.0782 | 76.2075 |  | 3582.2329 | 3334.0782 | 248.1547
7.5 | 5235.0877 | 5001.1173 | 233.9704 | 5001.1173 | 4881.1341 | 119.9832 |  | 5235.0877 | 4881.1341 | 353.9536
10 | 6963.8273 | 6668.1564 | 295.6709 | 6668.1564 | 6508.1788 | 159.9776 |  | 6963.8273 | 6508.1788 | 455.6485
15 | 10337.1824 | 9837.3626 | 499.8198 | 9837.3626 | 9688.3117 | 149.0509 |  | 10337.1824 | 9688.3117 | 648.8708
20 | 13487.0056 | 13116.4835 | 370.5221 | 13116.4835 | 12834.4086 | 282.0749 |  | 13487.0056 | 12834.4086 | 652.597
25 | 16707.7268 | 16147.1861 | 560.5406 | 16147.1861 | 15940.1709 | 207.0152 |  | 16707.7268 | 15940.1709 | 767.5558
30 | 19982.1429 | 19376.6234 | 605.5195 | 19376.6234 | 19128.2051 | 248.4182 |  | 19982.1429 | 19128.2051 | 853.9377
40 | 26465.6319 | 25668.8172 | 796.8147 | 25668.8172 | 25368.7566 | 300.0606 |  | 26465.6319 | 25368.7566 | 1096.8753
50 | 32683.4611 | 32086.0215 | 597.4396 | 32086.0215 | 31576.7196 | 509.3019 |  | 32683.4611 | 31576.7196 | 1106.7415
60 | 39006.5359 | 38256.4103 | 750.1257 | 38256.4103 | 37692.6316 | 563.7787 |  | 39006.5359 | 37692.6316 | 1313.9044
75 | 48811.3413 | 47566.4187 | 1244.9226 | 47566.4187 | 46918.239 | 648.1797 |  | 48811.3413 | 46918.239 | 1893.1023
100 | 64658.7216 | 63153.4392 | 1505.2824 | 63153.4392 | 62557.652 | 595.7872 |  | 64658.7216 | 62557.652 | 2101.0696
125 | 80911.0629 | 78941.7989 | 1969.264 | 78941.7989 | 78197.065 | 744.734 |  | 80911.0629 | 78197.065 | 2713.9979
150 | 96258.0645 | 94231.5789 | 2026.4856 | 94231.5789 | 93444.6764 | 786.9025 |  | 96258.0645 | 93444.6764 | 2813.3881
200 | 127657.754 | 125642.1053 | 2015.6487 | 125642.1053 | 124074.8441 | 1567.2612 |  | 127657.754 | 124074.8441 | 3582.9099
Size2 (hp) | Pre-EPAct Motors | NEMA Energy Efficient Motors | Energy Efficient → EPAct | NEMA Energy Efficient Motors | NEMA Prem Motors | Energy Efficient → NEMA Prem |  | Pre-EPAct Motors | NEMA Prem Motors | Energy Efficient → NEMA Prem
250 | 158386.4119 | 157052.6316 | 1333.7803 | 157052.6316 | 155093.5551 | 1959.0765 |  | 158386.4119 | 155093.5551 | 3292.8568
300 | 189661.0169 | 187672.956 | 1988.061 | 187672.956 | 186112.2661 | 1560.6899 |  | 189661.0169 | 186112.2661 | 3548.7508
350 | 220803.3827 | 218951.782 | 1851.6007 | 218951.782 | 217130.9771 | 1820.8048 |  | 220803.3827 | 217130.9771 | 3672.4055
400 | 251814.346 | 250230.608 | 1583.738 | 250230.608 | 248149.6881 | 2080.9198 |  | 251814.346 | 248149.6881 | 3664.6578
450 | 282992.6238 | 281509.434 | 1483.1899 | 281509.434 | 279168.3992 | 2341.0348 |  | 282992.6238 | 279168.3992 | 3824.2246
500 | 314436.2487 | 311482.2547 | 2953.994 | 311482.2547 | 310187.1102 | 1295.1445 |  | 314436.2487 | 310187.1102 | 4249.1385
1. This chart provides an estimated comparison of annual energy costs for Pre-EPAct, EPAct and NEMA Prem motors. Actual costs and savings may differ from the values shown.
2. The break in Motor Size between 200 and 250 hp occurs because EPAct applies to motors up to 200 hp. Above that value, NEMA's Energy Efficient Motor specification has been used as the reference.
3. The nominal efficiency values used in these calculations are defined as follows: Pre-EPAct Motors: DOE's MotorMaster+ software version 4.00.01 (9/26/2003) "Average Standard Efficiency" motor defaults ; EPAct Motors: Energy Policy Act of 1992 ; Energy Efficient Motors: NEMA MG 1-2003 Table 12-11 ; NEMA Premium Motors: NEMA MG 1-2003 Table 12-12. A table of all efficiency values is provided as the second tab of this Excel Workbook, Estimated Annual Energy Savings Chart, available at www.motorsmatter.org.

## TEFC Efficiency Values
Efficiency Values Used to Estimate Annual Energy Savings TEFC · 1800 RPM · Full-load Operation · Nominal Efficiency Estimated Annual Energy Cost = (Hp x annual operating hours x cost of electricity x 0.746) / (efficiency)
|  | Size (hp) | Pre-EPAct1 | EPAct2 | NEMA Premium4
|  | 1 | 76.68 | 82.5 | 85.5
|  | 1.5 | 79.08 | 84 | 86.5
|  | 2 | 80.83 | 84 | 86.5
|  | 3 | 81.4 | 87.5 | 89.5
|  | 5 | 83.34 | 87.5 | 89.5
|  | 7.5 | 85.51 | 89.5 | 91.7
|  | 10 | 85.73 | 89.5 | 91.7
|  | 15 | 86.63 | 91 | 92.4
|  | 20 | 88.52 | 91 | 93
|  | 25 | 89.3 | 92.4 | 93.6
|  | 30 | 89.56 | 92.4 | 93.6
|  | 40 | 90.19 | 93 | 94.1
|  | 50 | 91.32 | 93 | 94.5
|  | 60 | 91.75 | 93.6 | 95
|  | 75 | 91.68 | 94.1 | 95.4
|  | 100 | 92.25 | 94.5 | 95.4
|  | 125 | 92.19 | 94.5 | 95.4
|  | 150 | 93.03 | 95 | 95.8
|  | 200 | 93.54 | 95 | 96.2
|  | Size (hp) | Pre-EPAct1 | Energy Efficient3 | NEMA Premium4
|  | 250 | 94.22 | 95 | 96.2
|  | 300 | 94.44 | 95.4 | 96.2
|  | 350 | 94.56 | 95.4 | 96.2
|  | 400 | 94.83 | 95.4 | 96.2
|  | 450 | 94.88 | 95.4 | 96.2
|  | 500 | 94.86 | 95.8 | 96.2
1. Pre-Epact: DOE's MotorMaster+ software version 4.00.01 (9/26/2003) "Average Standard Efficiency" motor defaults
2. EPAct: Energy Policy Act of 1992
3. Energy Efficient: NEMA MG 1-2003 Table 12-11
4. NEMA Premium: NEMA MG 1-2003 Table 12-12

## ODP Annual Estimated Savings
Estimated Annual Energy Savings with NEMA Premium® Motors1 ODP · 1800 RPM · Full-load Operation · Nominal Efficiency3 Estimated Annual Energy Cost = (Hp x annual operating hours x cost of electricity x 0.746) / (efficiency)
Learn more about saving money through sound motor management. For additional tools and resources, visit www.motorsmatter.org.
|  | Enter Appropriate Values for: |  | Annual Operating Hours : |  |  | 8000 | hrs per year
|  |  |  | Cost of Electricity : |  |  | 10 | ¢ per kWh
Motor Size2 (hp) | Estimated Annual Operating Costs |  | Estimated Annual Energy Savings | Estimated Annual Operating Costs |  | Estimated Annual Energy Savings |  | Estimated Annual Operating Costs |  | Estimated Annual Energy Savings
| Pre-EPAct Motors | EPAct Motors | Pre-EPAct → EPAct | EPAct Motors | NEMA Prem Motors | EPAct → NEMA Prem |  | Pre-EPAct Motors | NEMA Prem Motors | Pre-EPAct → NEMA Prem
1 | 769.0722 | 723.3939 | 45.6782 | 723.3939 | 698.0117 | 25.3822 |  | 769.0722 | 698.0117 | 71.0605
1.5 | 1128.8777 | 1065.7143 | 63.1634 | 1065.7143 | 1034.9133 | 30.801 |  | 1128.8777 | 1034.9133 | 93.9644
2 | 1482.7329 | 1420.9524 | 61.7805 | 1420.9524 | 1379.8844 | 41.068 |  | 1482.7329 | 1379.8844 | 102.8485
3 | 2172.8155 | 2069.8266 | 102.9889 | 2069.8266 | 2000.4469 | 69.3797 |  | 2172.8155 | 2000.4469 | 172.3686
5 | 3560.8592 | 3410.2857 | 150.5735 | 3410.2857 | 3334.0782 | 76.2075 |  | 3560.8592 | 3334.0782 | 226.781
7.5 | 5253.5211 | 5057.6271 | 195.894 | 5057.6271 | 4918.6813 | 138.9458 |  | 5253.5211 | 4918.6813 | 334.8398
10 | 6931.475 | 6668.1564 | 263.3186 | 6668.1564 | 6508.1788 | 159.9776 |  | 6931.475 | 6508.1788 | 423.2962
15 | 10195.8998 | 9837.3626 | 358.5371 | 9837.3626 | 9625.8065 | 211.5562 |  | 10195.8998 | 9625.8065 | 570.0933
20 | 13517.5538 | 13116.4835 | 401.0703 | 13116.4835 | 12834.4086 | 282.0749 |  | 13517.5538 | 12834.4086 | 683.1452
25 | 16782.9021 | 16270.4471 | 512.455 | 16270.4471 | 15940.1709 | 330.2762 |  | 16782.9021 | 15940.1709 | 842.7312
30 | 20139.4826 | 19376.6234 | 762.8592 | 19376.6234 | 19026.5675 | 350.0559 |  | 20139.4826 | 19026.5675 | 1112.9151
40 | 26524.4444 | 25668.8172 | 855.6272 | 25668.8172 | 25368.7566 | 300.0606 |  | 26524.4444 | 25368.7566 | 1155.6878
50 | 32899.6692 | 32086.0215 | 813.6477 | 32086.0215 | 31576.7196 | 509.3019 |  | 32899.6692 | 31576.7196 | 1322.9497
60 | 39220.1533 | 38256.4103 | 963.7431 | 38256.4103 | 37692.6316 | 563.7787 |  | 39220.1533 | 37692.6316 | 1527.5218
75 | 48705.1143 | 47566.4187 | 1138.6956 | 47566.4187 | 47115.7895 | 450.6292 |  | 48705.1143 | 47115.7895 | 1589.3248
100 | 64799.1314 | 63421.8916 | 1377.2398 | 63421.8916 | 62557.652 | 864.2396 |  | 64799.1314 | 62557.652 | 2241.4794
125 | 80911.0629 | 78941.7989 | 1969.264 | 78941.7989 | 78197.065 | 744.734 |  | 80911.0629 | 78197.065 | 2713.9979
150 | 96465.5172 | 94231.5789 | 2233.9383 | 94231.5789 | 93444.6764 | 786.9025 |  | 96465.5172 | 93444.6764 | 3020.8408
200 | 128344.086 | 125642.1053 | 2701.9808 | 125642.1053 | 124592.9019 | 1049.2034 |  | 128344.086 | 124592.9019 | 3751.1841
Size2 (hp) | Pre-EPAct Motors | NEMA Energy Efficient Motors | Energy Efficient → EPAct | NEMA Energy Efficient Motors | NEMA Prem Motors | Energy Efficient → NEMA Prem |  | Pre-EPAct Motors | NEMA Prem Motors | Energy Efficient → NEMA Prem
250 | 158050.8475 | 156394.13 | 1656.7175 | 156394.13 | 155741.1273 | 653.0026 |  | 158050.8475 | 155741.1273 | 2309.7201
300 | 189260.0423 | 187672.956 | 1587.0863 | 187672.956 | 186889.3528 | 783.6032 |  | 189260.0423 | 186889.3528 | 2370.6895
350 | 221976.6206 | 218951.782 | 3024.8386 | 218951.782 | 218037.5783 | 914.2037 |  | 221976.6206 | 218037.5783 | 3939.0423
400 | 252080.2534 | 250230.608 | 1849.6455 | 250230.608 | 249185.8038 | 1044.8042 |  | 252080.2534 | 249185.8038 | 2894.4497
450 | 282694.7368 | 280334.0292 | 2360.7076 | 280334.0292 | 279168.3992 | 1165.6301 |  | 282694.7368 | 279168.3992 | 3526.3377
500 | 314105.2632 | 311482.2547 | 2623.0085 | 311482.2547 | 310187.1102 | 1295.1445 |  | 314105.2632 | 310187.1102 | 3918.153
1. This chart provides an estimated comparison of annual energy costs for Pre-EPAct, EPAct and NEMA Prem motors. Actual costs and savings may differ from the values shown.
2. The break in Motor Size between 200 and 250 hp occurs because EPAct applies to motors up to 200 hp. Above that value, NEMA's Energy Efficient Motor specification has been used as the reference.
3. The nominal efficiency values used in these calculations are defined as follows: Pre-EPAct Motors: DOE's MotorMaster+ software version 4.00.01 (9/26/2003) "Average Standard Efficiency" motor defaults ; EPAct Motors: Energy Policy Act of 1992 ; Energy Efficient Motors: NEMA MG 1-2003 Table 12-11 ; NEMA Premium Motors: NEMA MG 1-2003 Table 12-12. A table of all efficiency values is provided as the second tab of this Excel Workbook, Estimated Annual Energy Savings Chart, available at www.motorsmatter.org.

## ODP Efficiency Values
Efficiency Values Used to Estimate Annual Energy Savings ODP · 1800 RPM · Full-load Operation · Nominal Efficiency Estimated Annual Energy Cost = (Hp x annual operating hours x cost of electricity x 0.746) / (efficiency)
|  | Size (hp) | Pre-EPAct1 | EPAct2 | NEMA Premium4
|  | 1 | 77.6 | 82.5 | 85.5
|  | 1.5 | 79.3 | 84 | 86.5
|  | 2 | 80.5 | 84 | 86.5
|  | 3 | 82.4 | 86.5 | 89.5
|  | 5 | 83.8 | 87.5 | 89.5
|  | 7.5 | 85.2 | 88.5 | 91
|  | 10 | 86.1 | 89.5 | 91.7
|  | 15 | 87.8 | 91 | 93
|  | 20 | 88.3 | 91 | 93
|  | 25 | 88.9 | 91.7 | 93.6
|  | 30 | 88.9 | 92.4 | 94.1
|  | 40 | 90 | 93 | 94.1
|  | 50 | 90.7 | 93 | 94.5
|  | 60 | 91.3 | 93.6 | 95
|  | 75 | 91.9 | 94.1 | 95
|  | 100 | 92.1 | 94.1 | 95.4
|  | 125 | 92.2 | 94.5 | 95.4
|  | 150 | 92.8 | 95 | 95.8
|  | 200 | 93 | 95 | 95.8
|  | Size (hp) | Pre-EPAct1 | Energy Efficient3 | NEMA Premium4
|  | 250 | 94.4 | 95.4 | 95.8
|  | 300 | 94.6 | 95.4 | 95.8
|  | 350 | 94.1 | 95.4 | 95.8
|  | 400 | 94.7 | 95.4 | 95.8
|  | 450 | 95 | 95.8 | 96.2
|  | 500 | 95 | 95.8 | 96.2
1. Pre-Epact: DOE's MotorMaster+ software version 4.00.01 (9/26/2003) "Average Standard Efficiency" motor defaults
2. EPAct: Energy Policy Act of 1992
3. Energy Efficient: NEMA MG 1-2003 Table 12-11
4. NEMA Premium: NEMA MG 1-2003 Table 12-12